## Read me
Statutory maintenance checklist (UK)
Free checklist from graftum.com/building-maintenance-checklist · intervals checked against gov.uk, HSE and British Standard summaries on 24 October 2026.
How to use it
• One tab per frequency. Fill in Building, Last done and Next due; pick Evidence held from the dropdown.
• Next due is left for you to enter (your certificate or report states it). The shorter of the legal interval and the report's date always wins.
• Items marked 'England only' come from English regulations; Scotland and Wales have their own fire and housing law. HSE regulations (gas, LOLER, PSSR, asbestos, legionella, electricity at work) apply across Great Britain.
• General information, not legal advice. Where it says 'check the current regulation', do.
• Graftum's maintenance module keeps a PPM schedule like this per building and creates the task 7 days before it is due: graftum.com/maintenance
Building:
Reviewed by:
Date:

## Weekly
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Fire alarm — manual call point test (different call point each week, logged) | BS 5839-1 (recommendation); duty under Regulatory Reform (Fire Safety) Order 2005 art. 17 | Weekly | Trained on-site person |  |  | Not yet held | Log in the fire logbook; test at the same day/time each week.
Sprinkler system — alarm, valve and pressure checks | BS EN 12845 / LPC Rules; RRO 2005 art. 17 | Weekly | Trained on-site person |  |  | Not yet held | Follow the manufacturer's and installer's schedule — check the current standard.
Legionella — flush infrequently used outlets | HSE ACoP L8 / HSG274 Part 2 | Weekly | Trained in-house person |  |  | Not yet held | Record in the water hygiene log.

## Monthly
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Emergency lighting — short function (flick) test of every luminaire | BS 5266-1 / BS EN 50172; RRO 2005 art. 17 | Monthly | Trained on-site person |  |  | Not yet held | Check luminaires are clean, undamaged and light up on supply failure.
Legionella — hot and cold sentinel outlet temperatures; TMV checks | HSE ACoP L8 / HSG274 Part 2 | Monthly | Trained in-house person |  |  | Not yet held | Cold below 20°C within 2 minutes; hot at least 50°C within 1 minute (55°C in healthcare).
Fire extinguishers — visual check (in place, undamaged, pressure gauge, tamper seal) | BS 5306-3 (recommendation) | Monthly | Trained on-site person |  |  | Not yet held | More often where premises are open to the public.
High-rise residential (18 m+ or 7+ storeys) — firefighting lifts and firefighting equipment checks | Fire Safety (England) Regulations 2022 regs 7–8 | Monthly | Responsible person |  |  | Not yet held | Report defects not fixed within 24 hours to the fire and rescue service. England only.
Fire alarm — standby battery / generator checks | BS 5839-1 (recommendation) | Monthly | Trained on-site person |  |  | Not yet held | Vented batteries examined and topped up quarterly.

## Quarterly
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Fire doors in common parts — residential buildings over 11 m | Fire Safety (England) Regulations 2022 reg 10 | Quarterly | Responsible person (or competent contractor) |  |  | Not yet held | Check self-closers, gaps, seals, glazing, damage. England only.
Legionella — shower heads and hoses cleaned and descaled | HSE HSG274 Part 2 | Quarterly (or as risk assessment sets) | Trained in-house person |  |  | Not yet held

## Six-monthly
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Fire alarm — periodic inspection and servicing | BS 5839-1 (recommends at least two service visits a year); RRO 2005 art. 17 | Every 6 months | Competent fire alarm engineer |  |  | Not yet held | Certificate of inspection and servicing at each visit.
Passenger lifts and lifting equipment that carries people; all lifting accessories — thorough examination | LOLER 1998 reg 9 | Every 6 months (or per written examination scheme) | Competent person (usually the insurer's engineer surveyor) |  |  | Not yet held | Report of thorough examination kept until the next report, at least 2 years.
Legionella — cold water ball valve outlet temperatures | HSE HSG274 Part 2 | Every 6 months | Trained in-house person |  |  | Not yet held
Automatic opening vents (AOV) / smoke control — service | BS 7346 / BS EN 12101; RRO 2005 art. 17 | Typically every 6 months | Competent smoke-control engineer |  |  | Not yet held | Interval set by the manufacturer and the fire risk assessment — check.

## Annual
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Gas safety check — every gas appliance and flue in rented property (CP12 / Landlord Gas Safety Record) | Gas Safety (Installation and Use) Regulations 1998 reg 36 | Every 12 months (may be done up to 2 months early and keep the anniversary) | Gas Safe registered engineer |  |  | Not yet held | Copy to tenants within 28 days; keep records at least 2 years.
Emergency lighting — full-duration (3-hour) test | BS 5266-1 / BS EN 50172 | Every 12 months | Competent engineer |  |  | Not yet held | Fix failed luminaires; certificate and logbook entry.
Fire extinguishers — basic service | BS 5306-3 | Every 12 months (± 1 month) | Competent extinguisher service engineer |  |  | Not yet held | Extended service: 5 years water/foam/powder, 10 years CO2.
Fire risk assessment — review | Regulatory Reform (Fire Safety) Order 2005 art. 9 (review 'regularly' — no fixed interval; annual review is common practice) | Review at least yearly, and after any significant change | Competent fire risk assessor |  |  | Not yet held | Since 1 Oct 2023 (Building Safety Act s.156) the full assessment and findings must be recorded, whatever the size of the premises.
Flat entrance fire doors — residential buildings over 11 m | Fire Safety (England) Regulations 2022 reg 10 | Every 12 months (best endeavours) | Responsible person |  |  | Not yet held | England only.
Asbestos — re-inspection of known asbestos-containing materials and register review (pre-2000 non-domestic and communal areas) | Control of Asbestos Regulations 2012 reg 4 (duty to manage); HSE guidance: re-inspect at least every 12 months | Every 12 months (more often for higher-risk materials) | Duty holder; surveys by a competent (UKAS-accredited) surveyor |  |  | Not yet held | Keep the asbestos register and management plan for the life of the building.
Lightning protection system — inspection and test | BS EN 62305-3 (recommendation); Electricity at Work Regulations 1989 | Every 12 months (industry practice uses an 11-month cycle) | Specialist lightning protection engineer |  |  | Not yet held | Not a stand-alone statutory interval — check the current standard.
Legionella — cold water storage tank and calorifier internal inspection | HSE HSG274 Part 2 | Every 12 months | Competent water hygiene contractor |  |  | Not yet held
Goods lifts, hoists and other lifting equipment not carrying people — thorough examination | LOLER 1998 reg 9 | Every 12 months (or per written examination scheme) | Competent person |  |  | Not yet held
Sprinkler system — annual service | BS EN 12845 / LPC Rules | Every 12 months | Competent sprinkler engineer |  |  | Not yet held | Check the current standard and the insurer's requirements.
Hose reels — full inspection and test under pressure | BS EN 671-3 | Every 12 months (pressure test every 5 years) | Trained and competent person |  |  | Not yet held
Display Energy Certificate — public buildings over 250 m² | Energy Performance of Buildings (England and Wales) Regulations 2012 | Every 12 months (over 1,000 m²); every 10 years (250–1,000 m²) | Accredited energy assessor |  |  | Not yet held | Public authority buildings frequently visited by the public only.

## Multi-year
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
EICR (fixed wiring) — privately rented homes in England | Electrical Safety Standards in the Private Rented Sector (England) Regulations 2020 | At least every 5 years (or as the report states) | Qualified and competent person (e.g. C&G 2391 or equivalent) |  |  | Not yet held | Copy to tenants within 28 days, to a new tenant before they move in, to the council within 7 days if asked; remedial work within 28 days. Extended to social housing in 2025.
EICR (fixed wiring) — commercial and industrial premises | Electricity at Work Regulations 1989 reg 4(2); BS 7671 / IET Guidance Note 3 recommended maximum intervals | 5 years commercial; 3 years industrial; 1 year for some higher-risk premises | Qualified and competent electrician |  |  | Not yet held | The report itself sets the next inspection date — the shorter interval wins.
Legionella risk assessment — full review | HSE ACoP L8 / HSG274 Part 2 | Review regularly and after any system change (2-yearly review is common practice; no fixed legal interval) | Competent legionella risk assessor |  |  | Not yet held | Keep the written scheme of control up to date.
Air-conditioning inspection (TM44) — systems over 12 kW total cooling capacity | Energy Performance of Buildings (England and Wales) Regulations 2012 (inspection of air-conditioning systems) | At least every 5 years | Accredited energy assessor |  |  | Not yet held | Keep the report and hand it to a new owner or operator — check the current regulation.
Pressure systems — boilers, compressed air receivers, steam — examination under a written scheme | Pressure Systems Safety Regulations 2000 regs 8–9 | Intervals set by the written scheme of examination (often 12–14 months for boilers; up to 26 months for some systems) | Competent person (usually the insurer's engineer) |  |  | Not yet held | No written scheme = the system may not lawfully be operated.
Fire extinguishers — extended service / overhaul | BS 5306-3 | Every 5 years (water, foam, powder); every 10 years (CO2) | Competent extinguisher service engineer |  |  | Not yet held
Energy Performance Certificate | Energy Performance of Buildings (England and Wales) Regulations 2012 | Valid 10 years; needed on sale or letting | Accredited energy assessor |  |  | Not yet held | Minimum rating E to let (MEES) — check the current regulation.

## Other
Item | Legislation / standard | Frequency | Competent person | Last done | Next due | Evidence held | Notes
Smoke alarms (every storey with living accommodation) and CO alarms (any room with a fixed combustion appliance, excluding gas cookers) — rented homes | Smoke and Carbon Monoxide Alarm (England) Regulations 2015, amended 2022 | Checked working at the start of each tenancy; repair or replace as soon as told they are faulty | Landlord or agent |  |  | Not yet held | Social landlords included from 1 Oct 2022. Penalty up to £5,000 — check the current regulation.
Portable appliance testing (PAT) and user checks | Electricity at Work Regulations 1989 reg 4 (not a fixed statutory test interval) | Risk-based: user checks before use; formal visual inspection and test as the risk assessment sets (often yearly in offices, more often on sites) | Competent person |  |  | Not yet held | HSE: no legal requirement to PAT test every year — frequency follows risk.
Asbestos — refurbishment and demolition survey before any intrusive work | Control of Asbestos Regulations 2012 regs 4–5 | Before every refurbishment or demolition | Competent (UKAS-accredited) surveyor |  |  | Not yet held
Building Safety Act — safety case report, golden thread information, resident engagement strategy (higher-risk buildings: 18 m+ or 7+ storeys with 2+ residential units) | Building Safety Act 2022 ss. 65, 83–91; Higher-Risk Buildings (Keeping and Provision of Information etc.) (England) Regulations 2024 | Keep up to date continuously; register the building with the Building Safety Regulator; Building Assessment Certificate when called | Principal accountable person |  |  | Not yet held | England only — check the current regulation.
Employers' liability insurance certificate | Employers' Liability (Compulsory Insurance) Act 1969 | Renew yearly; certificate displayed or available electronically | Employer |  |  | Not yet held | HSE recommends keeping old certificates for 40 years.